Section 26 33 23

Centralized Emergency Lighting Inverter

- Guide Specification for 600W – 2KW Systems

- (Optional Items in Red)

PART 1 - GENERAL

1.1	DESCRIPTION

This specification defines the electrical and mechanical characteristics and requirements for a stored electrical energy, uninterruptible, emergency power supply system. The system as specified herein includes all the components required to deliver reliable, high quality uninterruptible power for emergency illumination and related life safety equipment. The system shall incorporate an online, dual conversion, advanced DSP controlled, high frequency, IGBT PWM rectifier/charger and inverter, high speed automatic bypass transfer device, battery charging system, energy storage battery platform, a diagnostic monitoring display panel, and all the related hardware components and software to facilitate a functional centralized system. The emergency power supply system shall provide immunity from all line disturbances and power interruptions. The system includes an uninterrupted, normally on output power section and a normally off standby output power section, thus enabling compatibility with emergency lighting fixtures operating in normally on and standby mode(s). A self-diagnostic monitoring alarm system continuously advises of system status and battery condition.

- 1.2	STANDARDS

The system shall be designed in accordance with applicable portions of the following standards:

- American National Standards Institute (ANSI C57.110)

- Institute of Electrical and Electronic Engineers (IEEE 519-1992) (C62.41-1991)

- National Electrical Manufacturers Association (NEMA PE-1)

- National Electric Code (NEC 2005, Article 700)

- National Fire Protection Association (NFPA 70) (NFPA 101) (NFPA 111)

- Underwriters Laboratories (UL 924)

- Federal Communications Commission (FCC Part 15, Sec. J, Class A)

- Federal Aviation Administration (FAA-G-201e)

- Listed UL Standards UL 924 Emergency Lighting Equipment with 90 minutes, or UL 924 Auxiliary Lighting and Power Equipment for other than 90 minutes battery backup, or C-UL listed with 30 minutes to CSA Standard C22.2 No. 141-02, Canadian Electrical Code, Part I, and the National Building Code of Canada.

  - SUBMITTALS

A.          Manufacturer Requirements:

- The manufacturer shall be ISO 9001:2008 “Quality Assurance Certified” and shall upon request furnish certification documents.

- The manufacturer shall be a United States based manufacturer with 5 years experience or greater in design and fabrication of centralized stored electrical energy emergency and standby power systems.

B.          Product Data:

- The manufacturer shall supply documentation for the installation of the system, including wiring diagrams and cabinet outlines showing dimensions, weights, BTUs, input/output current, input/output connection locations and required clearances.

- Factory test results shall be provided to show compliance with the requirements. The manufacturer shall include battery test documentation which demonstrates compliance with the specified minimum emergency reserve with full rated KW load.

- The supplier shall furnish (6) equipment submittal copies. Submittals shall be specific for the equipment furnished and shall include as-built information.

PART 2 - PRODUCTS

- 2.1	Manufacturers

The equipment specified shall be the UltraLITE Model ELC centralized emergency lighting inverter system, manufactured by Trystar.

2.2         Manufactured Units

    - The system shall be designed and manufactured to assure maximum reliability, serviceability and performance. All control devices and system electronics shall be accessible via the front inverter cabinet for rapid service or replacement. The diagnostic monitor panel display shall be mounted on the front of the system for easy observation of system status and battery condition. The system is to be furnished with an internally located AC input circuit breaker and up to 12 output circuit breakers as specified. The battery and DC conductors shall be DC circuit breaker protected. All conductors and transformer windings shall be copper constructed. The installed system shall be floor mounted and wall secured, constructed of steel, with the inverter controls, bypass, and breakers being front accessible through a hinged door, requiring a hand tool for access. The installed inverter cabinet shall be designed to meet NEMA 2 standards, rated for indoor use. Cabinet dimensions shall not exceed (22” W x 12”D x 40”H) (22” W x 12”D x 50”H) (22” W x 12”D x 74.5”H).

    - The system shall operate in accordance with requirements as specified herein to support any combination of fluorescent ballast fixtures, incandescent lamps, electronic and high power factor fluorescent ballasts, LED or HID fixtures or other approved loads up to the rating of the system. “Normally on” and “Normally off” AC output bus shall be 100% rated and limited only by the system’s maximum KW output rating.

    - Normal Operation: The load is supplied with regulated power derived from the normal AC power input terminals through the rectifier charger and inverter. The rectifier charger shall be fully rated to charge the batteries and supply sufficient DC energy for the inverter when under full load. The battery shall be connected in parallel with the rectifier charger output.

    - Uninterrupted Emergency Operation: Upon the failure or unacceptable deviation of commercial AC power, energy will be supplied by the battery through the inverter and continue to supply power to the load without switching loss or disturbance. When power is restored at the AC input terminals of the system, the rectifier charger shall continue to supply power to the load through the inverter and simultaneously recharge the batteries. There shall be no break or interruption of power to the load upon failure or restoration of the commercial AC power.

    - Standby Emergency Operation: Upon the failure or unacceptable deviation of commercial AC power or upon a remote input “command on signal”, the standby, normally off AC output section of the system shall become energized, thus providing emergency power for standby lighting fixtures which are required to illuminate only in the event of emergency. User-adjustable settings shall include transfer on delay time (0 to 8 seconds), transfer off delay time (0 to 15 minutes), and a soft start control (0 to 172 cycles) to accommodate the high inrush current associated with energizing normally off emergency lights, compatible with various lighting types and manufacturers.

    - Automatic Bypass Operation: The system shall include a high speed automatic bypass for fault clearing, for instantaneous overload conditions and/or to connect the load to the normal utility source in the event of a system rectifier charger or inverter failure.

    - Manual Bypass Switch: The system shall include an integral inverter bypass switch for use in case of an inverter failure. The switch shall be accessible via the front of the inverter enclosure, through a hinged door, requiring a hand tool for access. When in the bypass position, the switch shall bypass the inverter power control electronics and divert utility power to the inverter’s normally on output bus.

    - System Power Output Capability: The stored emergency power supply system output power rating shall be  (600 watts) (1000 watts) (1500 watts) (2000 watts).

    - Battery Time Reserve Capacity: Battery shall be capable of producing emergency power for (_) (30) (60) (90) (120) (240) minutes at full rated watts.

    - Reliability: MTBF 100,000 hours. MTTR, 1 hour typical.

    - System Input Breaker Rating: Input breaker shall be sized to accommodate full rated load, low line input, and maximum recharge current simultaneously. (600 watt unit – 10A @ 120 VAC or 15A @ 277 VAC)   (1000 watt unit – 20A @ 120 VAC or 10A @ 277 VAC) (1500 watt unit – 25A @ 120 VAC or 15A @ 277 VAC) (2000 watt unit – 30A @ 120 VAC or 15A @ 277 VAC).

2.3         Input Specifications

- Input Voltage: 120 VAC or 277 VAC.

- Input Voltage Operating Range:  +12% to -15% at full load without battery usage.

- Extended Range: The unit shall incorporate the use of variable range logic in conjunction with the load percentage to extend the input range up to +12% to -30%, without battery usage, while maintaining a regulated output voltage.

- Frequency Range:  57.5 hertz to 62.5 hertz.

- Power Factor:  Self correcting to >0.97 (approaching unity).

- Input Current Harmonics:  <5% THD (total harmonic distortion).

- System AIC (Amperes Interrupting Current) Rating: 10kAIC.

2.4         Output Specifications

- Output Voltage: 120 VAC or 277 VAC.

- Sine Wave Voltage:  Maximum 3% THD under linear load.

- Frequency: 60 hertz + 0.5% under full load while in the battery operation mode.

- Harmonic Attenuation: Reflected load generated harmonics shall be attenuated at the input.

- Voltage Regulation: +/-2%.

- Output Power Rating: KVA at 1.0 power factor (unity). KVA = KW

2.5	Battery Specifications

- Battery time: (90 Minutes at full rated kilowatt output, UL 924 listed Emergency Lighting Equipment) (30 Minutes at full rated kilowatt output, C-UL listed to CSA Standard C22.2 No. 141-02) ( ___ Minutes at full rated kilowatt output, UL 924 listed Auxiliary Lighting and Power Equipment).

- Battery Type:  Integral, valve regulated, sealed lead calcium, maintenance free.

- Charger:  4 stage, 400 watts, temperature compensated, smart charge.

- Recharge Time:  UL 924, NFPA 101 compliant, 24 hour recharge.

- Bus Voltage:  72 VDC.

2.6         Performance Specifications

- Overload Rating (without use of static bypass):  Up to 102% continuous, 125% for 30 cycles, 150% for 4 cycles when fed from the AC power source, or on battery.

- LED Inrush Rating (without use of static bypass):   Peak overload capability of 1200% during a current surge of ¼ cycle, when fed from the AC power source or on battery, to accommodate inrush current from LED fixtures/drivers.

- Fault Clearing (with bypass available): 150% for 1 minute, 500% for 1 second, 1000% for 1 cycle.

- Normally Off Bus Output with User-Progammable Soft-Start: Adjustable settings shall be provided to limit the high inrush current, associated with energizing normally off emergency lights, to within the inverter’s on battery overload rating.

- Voltage Regulation: The output voltage shall be regulated to within +2% during input voltage changes from +12% to -15% with reference to nominal, and when the output is loaded from no load to full rated load.

- Reactive Power Correction:  Load at .6 pF corrected to > 0.97 at input (automatically correcting).

- Efficiency: 88% typical under full rated load.

- Reliability: 100,000 hours MTBF.

2.7	Environmental Specifications

- Operating Temperature:  (20°C to 35°C for UL 924 Listed models – Emergency Lighting Equipment.) (0°C to 40°C for UL 924 Listed models – Auxiliary Lighting and Power Equipment Listed.) (10°C to 40°C for C-UL Listed models.) Optimum battery performance and life shall be achieved at 25°C. Inverter electronics shall be designed for use at 0°C to 40°C.

- Inverter Storage Temperature:  -20°C to 50°C.

- Battery Storage Temperature:  25°C for 6 months. For each 9°C rise, reduce storage time by half.

- Relative Humidity:  95% non-condensing.

- Elevation:  5,000 feet, 1,500 meters.

- Weight and Cabinet Sizes for UL 924 Listed models with 90 Minutes:

Rating / Voltage	         Weight (lb.) 	Dimensions W x D x H

600 / 120 - 120		269		22” x 11.75” x 40”

600 / 120 - 277		286		22” x 11.75” x 40”

600 / 277 - 120		286		22” x 11.75” x 40”

600 / 277 - 277		303		22” x 11.75” x 40”

1000 / 120 - 120		352		22” x 11.75” x 50”

1000 / 120 - 277		369		22” x 11.75” x 50”

1000 / 277 - 120		369		22” x 11.75” x 50”

1000 / 277 - 277		386		22” x 11.75” x 50”

1500 / 120 - 120		372		22” x 11.75” x 50”

1500 / 120 - 277		402		22” x 11.75” x 50”

1500 / 277 - 120		402		22” x 11.75” x 50”

1500 / 277 - 277		432		22” x 11.75” x 50”

2000 / 120 - 120		534		22” x 11.75” x 50”

2000 / 120 - 277		564		22” x 11.75” x 50”

2000 / 277 - 120		564		22” x 11.75” x 50”

2000 / 277 - 277		594		22” x 11.75” x 50”

- Audible Noise Level: Not greater than 50 dba at 3 feet.

- Enclosure: NEMA 2, powder-coat painted steel construction, drip-proof, and sealed prohibiting rodent entry.

2.8	 Display Monitor and Diagnostics

    - Display Panel – System shall include a local, front mounted, sealed, LED display panel to indicate system status and battery condition. Display shall include provisions to automatically monitor inverter input voltage normal, inverter input voltage high, inverter input voltage low,  inverter on automatic bypass, % load, battery in use, battery full charge, battery low and check battery.

    - Audible Alarm – The display panel includes an audible alarm with alarm silence for system on battery, low battery, check battery, over temperature warning, system fault and inverter overload.

    - Control Functions –  Push button for inverter on, fail safe dual push buttons for inverter off, alarm silence push button and push button for manually initiating a system battery test.

    - Communications Port (RS232) – Include a DB9 and USB communications port for remote monitoring access to electrical measurements, system set point programming and system logs.

    - Electrical Measurements (RS232) – Electrical measurements shall include: input voltage L1-neutral, output voltage L1-neutral, output current (amps), output watts, output volt amperes, % load, battery voltage and DC charging current, and output frequency.

    - System Set Points (RS232) – Include provision to program the following: low battery alarm, battery usage, automatic battery tests programmable for 30 day intervals, or 90 day intervals and an annual discharge test. The start date and time of the 30, or 90 day test selected and of the annual test (365 day interval) shall be programmable via the RS232 connection (DB9 or USB port). The time duration of the automatic battery test shall be programmable (30 seconds or 5 minutes).

    - System Log (RS232) – System shall include provisions to log power outages, system overloads and battery test pass/fail results, all with a date and time stamp.

    - Automatic Self-Testing – Systems shall provide a programmable 30 second (battery runtimes less than 30 minutes) or 5 minute automatic battery test that can be programmed to occur every 30, or 90 days.

2.9	Relay Communications Interface

- Status / Alarm relay interface normally open contacts shall be provided for optional remote annunciator panel or automatic message dialer. Include potential free, 120 VAC @ .5amps, contacts for inverter on battery, low battery warning, and general alarm.

- A normally closed Battery Test Active contact shall be provided that opens during automatic or manual system testing. This contact shall be used to signal one or more UL924 listed shunt relays to bypass local control devices during periodic and annual NFPA-mandated tests, in order to provide emergency power to designated emergency lighting fixtures.

2.10	Accessories (Optional Equipment)

    - Include remote annunciator panel for remote status indication of system alarm conditions including system on emergency battery power, low battery warning, and general alarm.

    - Include (Quantity) control device (dimmer control, wall switch, occupancy sensor) override(s) for use with normally on inverter output bus to provide full illumination to designated emergency lights upon the failure or loss of commercial AC power.

    - Include (Quantity) zone sensing device(s) to sense voltage at individual zone lighting panels. The sensing device shall detect loss of power at the panel and shall signal the system to illuminate emergency fixtures within the specific zone only. If commercial AC power is acceptable at other zones, emergency lighting shall remain in the standby mode.

    - Include network device SNMP / Ethernet TCP/IP adapter for network communication of inverter system status, electrical measurement data, and automatic battery pass / fail test results with time and date stamp.

    - Include network device SNMP / MODBUS TCP / Ethernet TCP/IP adapter for network communication of inverter system status, electrical measurement data, and automatic battery pass / fail test results with time and date stamp.

    - Include network device SNMP / MODBUS RS485 / Ethernet  TCP/IP adapter for network communication of inverter system status, electrical measurement data, and automatic battery pass / fail test results with time and date stamp.

    - Include (quantity) pre-installed, (15 amp) (20 amp), single pole, output circuit breakers for use with normally on AC output bus. (Note: A total of 12 breakers or 6 monitored breakers, factory-wired to the normally on and/or optional timed normally off output bus, in any combination. If 277V output, only select 15 amp circuit breakers. If 120V output, 15 amp or 20 amp circuit breakers may be selected.)

    - Include (quantity) pre-installed, (15 amp) (20 amp), single pole, output circuit breakers for use with timed normally off AC output bus. (Note: A total of 12 breakers or 6 monitored breakers, factory-wired to the normally on and/or optional timed normally off output bus, in any combination. If 277V output, only select 15 amp circuit breakers. If 120V output, 15 amp or 20 amp circuit breakers may be selected.)

    - Include output circuit breaker open or tripped alarm contacts on all output circuit breakers for use with remote and/or local annunciation indicators. (Max 12 pole positions between the normally on and normally off bus, each alarm contact added requires 1 pole position. 120V and 277V breakers only)

2.11	Warranty

    - The manufacturer shall guarantee all power component and system electronics to be free from defects in material and workmanship for a period of 2 years following shipment from the factory.

    - Battery warranty shall be 1 year full replacement, 14 year prorated.

2.12	Serviceability

The inverter’s power section, including all control cards and system electronics, shall be front-accessible and located behind a secure hinged access door for ease of service or component replacement. An integral inverter bypass switch must be provided. A DC circuit breaker and DC Anderson connector shall be incorporated into the design to facilitate rapid replacement of the batteries via the front of the system enclosure. No side access shall be required. To facilitate inverter diagnostics and programming, a DB9 and USB communications port shall be provided for access to electrical measurements, system set points, and system logs.