Section 26 33 23

UltraLITE Model ELU Centralized Emergency Lighting Inverter

- Guide Specification for 1.5 KW – 14 KW Systems

- with Advanced Monitor

- (Optional Items In Red)

- Part 1

  - General

This specification defines the electrical and mechanical characteristics and requirements for an uninterruptible stored emergency power supply system. The system as specified herein includes all the components required to deliver reliable, high quality uninterruptible power for emergency illumination and related life safety equipment. The system shall incorporate an on-line, dual conversion,  microprocessor controlled, high frequency, IGBT PWM rectifier/charger and inverter, high speed automatic bypass transfer device, battery charging system, energy storage battery platform, an advanced, full diagnostic, monitoring and testing system with touch screen LCD display panel, and all the related hardware components and software to facilitate a functional centralized system. The emergency power supply system shall provide immunity from all line disturbances and power interruptions. The system shall include an uninterrupted, normally on output power section and provisions to include a normally off standby output power section, thus enabling compatibility with emergency lighting fixtures operating in normally on and standby mode(s). A self-diagnostic monitoring alarm system shall continuously advise of system status and battery condition.

  - Standards

The systems shall be designed in accordance with applicable portions of the following standards:

    - American National Standards Institute (ANSI C57.110).

    - Institute of Electrical and Electronic Engineers (IEEE 519-2014) (C62.41-2002).

    - National Electrical Manufacturers Association (NEMA PE-1).

    - National Electric Code (NEC 2005, Article 700).

    - National Fire Protection Association (NFPA 70) (NFPA 101) (NFPA 111).

    - NFPA 101 Section 7.9.3.1.3 – Periodic Testing of Emergency Lighting Equipment

    - Underwriters Laboratories (UL 924) (C-UL to CSA Standards).

    - Federal Communications Commission (FCC Part 15, Sec. J, Class A).

    - Federal Aviation Administration (FAA-G-201e).

    - Listed UL Standards - UL 924 Emergency Lighting Equipment with 90 minutes, (or UL 924 Auxiliary Lighting and Power Equipment for other than 90 minutes battery back up time), UL 1778 UPS Equipment, C-UL listing to CSA C22.2, No. 107.1-M01 Canadian Standards for UPS Equipment (or C-UL listed to CSA C22.2 No. 141-15 Emergency Lighting Equipment with 30 minutes).

Inverter system shall be seismic-rated, designed and tested in accordance with applicable portions of the following

additional standards:

    - ICC - AC156: “Acceptance Criteria for Seismic Certification by Shake-Table Testing of Nonstructural Components and Systems”

    - ASCE 7-10

    - California Building Code – CBC 2016

    - International Building Code – IBC 2015

  - Submittals

    - The manufacturer shall supply documentation for the installation of the system, including wiring diagrams and cabinet outlines showing dimensions, weights, BTUs, input/output current, input/output connection locations and required clearances.

    - The manufacturer shall be a “Quality Assurance Certified” ISO 9001:2015 company, and shall upon request furnish certification documents.

    - The manufacturer shall be a United States based manufacturer with 10 years experience or greater in design and fabrication of centralized stored electrical energy emergency and standby power systems.

    - Factory test results shall be provided to show compliance with the requirements. The manufacturer shall include battery test documentation to validate the specified minimum emergency reserve with full rated KW load.

    - The supplier shall furnish (6) equipment submittal copies. Submittals shall be specific for the equipment furnished and shall include as-built information.

    - The manufacturer shall supply a seismic testing certificate of compliance to validate that the system was shake-table tested and met the code requirements specified.

Part 2

- 2.1	Manufacturers

The equipment specified shall be the UltraLITE  Model ELU centralized emergency lighting inverter system, manufactured by Trystar.

2.2        Manufactured Units

The system shall be designed and manufactured to assure maximum reliability, serviceability and performance. The system shall include one main control module for rapid service or replacement. The local display shall be mounted on the front of the system for easy observation of system status and battery condition. The system is to be furnished with an internally located AC input circuit breaker and output distribution panel. The battery and DC conductors shall be DC fuse protected. All conductors and transformer windings shall be copper constructed. Cabinets are floor mountable, constructed of  steel, front accessible through a hinged,  key lockable door and shall be NEMA 1 rated for indoor use. The system shall be seismic-rated and provided with seismic brackets.

    - Systems shall operate in accordance with requirements as specified herein to support any combination of LED lighting, fluorescent ballast fixtures, incandescent lamps, electronic and high power factor fluorescent ballasts, HID fixtures or other approved loads up to the rating of the system. “Normally on” and “Normally off” AC output bus shall be 100% rated and limited only by the system maximum KW output rating.

    - Normal Operation: The load shall be supplied with regulated power derived from the normal AC power input terminals through the rectifier charger and inverter. The rectifier charger shall be fully rated to charge the batteries and supply sufficient DC energy for the inverter when under full load. The battery shall be connected in parallel with the rectifier charger output.

    - Uninterrupted Emergency Operation: Upon the failure or unacceptable deviation of commercial AC power, energy shall be supplied by the battery through the inverter and continue to supply power to the load without switching loss or disturbance. When power is restored at the AC input terminals of the system, the rectifier charger shall continue to supply power to the load through the inverter and simultaneously recharge the batteries. There shall be no break or interruption of power to the load upon failure or restoration of the commercial AC power.

    - Standby Emergency Operation (Optional): Upon the failure or unacceptable deviation of commercial AC power or upon a remote input command signal, the standby,  normally off AC output section of the system shall become energized thus providing emergency power for standby lighting fixtures which are required to illuminate only in the event of emergency. Field adjustable timers shall be included for use with on and off delay transition requirements.

    - Automatic Bypass Operation: The system shall include an automatic bypass switch for fault clearing, instantaneous overload conditions and/or to connect the load to the normal utility source in the event of a system rectifier charger or inverter failure.

    - Secure Bypass Switch: The system shall include an integral, secure, make-before-break  bypass switch accessible via the front of the inverter enclosure through a hinged, key lockable door. The secure bypass switch shall incorporate a push-to-turn function.   Pushing the bypass switch shall invoke the inverter’s static bypass and indicate that it is safe to turn the switch to the bypass mode. The secure bypass switch shall provide complete isolation of the inverter output terminals from external circuits. When the load is supplied from the utility through the secure bypass switch, the AC supply terminals shall remain energized to permit operational checking of the inverter, but the inverter output shall remain isolated from the load.

    - System Power Output Capability: The stored emergency power supply system output power rating shall be   (1.5) (2.2) (3.0) (3.5) (4.2) (5.0) (6.0) (7.0) (7.5) (8.5) (10) (12.5) (13.5) (14) KW.

    - Battery Time Reserve Capacity: Battery shall be capable of producing emergency power for (__) (30) (60) (90) (120) (240) minutes at full rated watts.

    - Reliability: MTBF 100,000 hours. MTTR, 1 Hour.

Part 3

3.1	Input Specifications

3.1.1	Input Voltage:  _________ VAC.

(Input Voltage Selection)

1.5 – 2.2 KW:  (120) (277)

3.0 – 3.5 KW:  (120) (208/120) (240/120) (277)

4.2 – 5.0 KW:  (120) (208/120) (240/120) (277) (347) (480) (600)

6.0 – 14 KW:   (208/120) (240/120) (277) (347) (480) (600)

3.1.2		Input Voltage Operating Range:  +12% to -15% at full load without battery usage.

3.1.3		Extended Range: The unit shall incorporate the use of variable range logic in conjunction with the load percentage to extend the input range up to +12% to -30% without battery usage while maintaining a regulated, usable output voltage.

3.1.4	Frequency Range:  57.5 Hz to 62.5 Hz.

3.1.5	Power Factor:  Self correcting to >0.97 (approaching unity).

3.1.6	Input Current Harmonics:  <5% THD (total harmonic distortion).

3.1.7	System AIC (Amperes Interrupting Current) Rating: 65k AIC.

3.2	Output Specifications

- 3.2.1	Output Voltage:  _________ VAC.

(Output Voltage Selection)

- 1.5 – 2.2 KW:  (120) (277) (277/120)

- 3.0 – 3.5 KW:  (120) (208/120) (240/120) (277) (277/120)

- 4.2 – 5.0 KW:  (120) (208/120) (240/120) (277) (277/120) (347/120)

- 6.0 – 14 KW:   (208/120) (240/120) (277) (277/120) (347/120)

- 3.2.2   	Sine Wave Voltage:  Maximum 3% harmonic distortion under linear load.

- 3.2.3	Frequency: 60 hertz + 0.5% under full load while in the battery operation mode.

3.2.4	Harmonic Attenuation: Reflected load generated harmonics shall be attenuated at the input.

    - Voltage Regulation: +/-2%.

    - Output Power Rating: KVA at 1.0 power factor (unity). KVA = KW

3.3	Battery Specifications

3.3.1	Battery time: 90 Minutes at full rated kilowatt output capability, UL 924 Listed as Emergency Lighting Equipment. ( ____ minutes at full rated kilowatt capability, UL 924 Listed as Auxiliary Lighting and Power Equipment.) (30 minutes at full rated kilowatt capability, C-UL listed to CSA C22.2 No. 141-15 Emergency Lighting Equipment.)

3.3.2	Battery Type:  Integral, valve regulated, sealed lead calcium, maintenance free.

3.3.3	Charger:  4 stage, temperature compensated, 1% ripple filtered.

3.3.4	Recharge Time:  24hrs, UL 924, NFPA 101 complaint.

3.3.5	Bus Voltage:  120 VDC.

3.4	Performance Specifications

    - Overload Rating (without use of static bypass): Up 125% for 30 cycles, 150% for 4 cycles when fed from the AC power source, or on battery.

    - LED Inrush Rating (without use of static bypass):  Peak overload capability up to 1400% during a current surge of ¼ cycle, when fed from the AC power source or on battery, to accommodate inrush current from LED fixtures/drivers.

    - Fault Clearing (with bypass available): 125% for 2 minutes, 150% for 30 seconds and 200% for 15 cycles when fed from AC power source.

    - Voltage Regulation: The output voltage shall be regulated to within +2% during input voltage changes from +12% to – 15% with reference to nominal, and when the output is loaded from no load to full rated load.

    - Common Mode (isolation transformer units only):  120 dB (106 : 1 ground noise attenuation).

    - Transverse Mode (isolation transformer units only):  70 dB (3160 : 1 line noise attenuation).

    - Reactive Power Correction:  Load at .6 pf corrected to > 0.97 at input (automatically correcting).

    - Reliability: 100,000 hours MTBF.

3.5	Environmental Specifications

3.5.1	Operating Temperature: UL 924 listed Emergency Lighting Equipment at 20°C (68°F) to 30°C (86°F).

C-UL listed to CSA C22.2 No. 141-15 with 30 minutes at 20°C (68°F) to 30°C (86°F).

UL 924 Auxiliary Lighting and Power Equipment, UL 1778, and C-UL listed to CSA C22.2 No.107.1-01 at 0°C (32°F) to 40°C (104°F).

- 3.5.2	Storage Temperature:  -20°C to 50°C

3.5.3	Relative Humidity:  95% non-condensing.

3.5.4	Elevation:  5000 feet, 1500 meters without de-rating.

3.5.5	Audible Noise Level: Not greater than 50 dba at 1 meter.

    - Enclosure: NEMA 1

Part 4

4.1	 Display Monitor and Diagnostics

    - Display Monitor –  A display monitor shall be included to uphold NFPA guidelines for emergency illumination, emergency back up time and unattended, periodic testing of the centralized emergency power system. The system shall include a local, front mounted, sealed, touch screen, LCD display monitor to verify system electrical and temperature measurements, inform/alarm for abnormal system status, allow programming of user specified set points and inform of periodic system and battery test results.

      - The monitor shall display the following electrical parameters. Note that L2 parameters shall be

displayed when applicable:

Input Voltage
			Output Voltage L1-N

Output Voltage L2-N

Output Current L1-N

Output Current L2-N

Output Volt-Amperes L1-N

Output Volt-Amperes L2-N

Output Volt-Amperes Total

Output Watts L1-N

Output Watts L2-N

Output Watts Total

Output Power Factor L1 – N

Output Power Factor L2 – N

Output Power Factor Total

Output Percent Load L1-N

Output Percent Load L2-N

Output Percent Load Total

Output Frequency

Battery Voltage	
			Battery Charger Current

      - The monitor shall display the following status and alarm conditions. Note that L2 alarm conditions

shall be displayed when applicable:

Input Voltage High/Low

Output Voltage L1-N High/Low

Output Voltage L2-N High/Low

Output Volt-Amperes High - Overload

Output Volt-Amperes Low

Output Frequency High/Low

Battery Voltage High/Low

Battery Charger Current High

General Alarm

System On Battery

Low Battery Warning

Low Battery Shutdown

Inverter Over-temperature Warning

DC Charger Failure / DC Open

Output Circuit Breaker Open

REPO Shutdown

System in Manual Bypass

System in Static Bypass

Battery Test Pass

Battery Test Fail

4.1.1.3	The monitor shall display the following operational conditions:

System Normal

Percent Battery Time Remaining

Battery Test In Process
			Off Bus Connecting

Off Bus Returning

    - Programming User Specified Set Points – Include provisions for user interface programming of system status  for high/low alarm threshold set points, programming of off bus delay timer(s), programming of periodic battery test duration with date and time and programming of annual battery test duration with date and time. Allow threshold adjustability limits to comply with NFPA and local code periodic battery and system reliability testing.

    - The monitor shall feature a manual, proprietary, password protected “Push to Test” feature.

    - Periodic Testing - The monitor shall feature diagnostics for automatic and manual battery testing.

      - It shall feature a 5 minute battery discharge test every 30 days or 90 days, and a user programmable annual battery discharge test of either 30 minutes, 60 minutes, 90 minutes, 120 minutes or 240 minutes.

      - It shall report the results of the battery test with a pass/fail indication, time and date stamped via the local monitor panel and/or via (E-mail, SNMP, Ethernet TCP/IP or MODBUS TCP or BACnet/IP ) (MODBUS RTU or ASCII over RS485, or BACnet MS/TP). (An optional Multifunction Communications Modem shall be provided so test results can be sent via fax, voice messaging and or web page generation.)

      - During the battery test, the monitor shall perform an egress lighting integrity test. The egress lighting  integrity test shall measure the KVA load on the output of the system and if the output load falls below the customer defined value, the inverter shall sound an audible and visual alarm, thus indicating fixture maintenance or component replacement.

    - Periodic Testing Log - The monitor shall maintain a historic log that sequentially records 25 battery tests which indicate time, date and pass/fail results. The log shall be made available through the LCD display of the monitor and remote communication capabilities.

    - Status Alarm Log - The monitor shall maintain a historic log that sequentially records 25 status alarms which indicate time and date of abnormal occurrences. The log shall be made available through the LCD display of the monitor and remote communication capabilities.

4.2	Communications

4.2.1	The monitoring system shall contain a  9 pin status / alarm port with potential free 24VAC and/or DC 500mA rated contacts and a terminal strip with potential  free, 120V 500mA rated contacts for use with an optional remotely located audible / visual annunciator panel, optional automatic message dialer, optional fax modem, or optional computer network integration adapter.

    - Alarm Port - Include provisions to remotely communicate and/or notify of system on battery power, low battery, general alarm and system on bypass.

    - Alarm Relay Contacts - Include hardwire terminal strip connections to alarm relay contacts that remotely communicate and/or notify of inverter on battery power, low battery, general alarm, system on bypass, battery test pass and battery test fail occurrences.

    - Battery Test Active Contact - A normally closed battery test active contact shall be provided that opens during automatic or manual system testing. This contact shall be used to signal one or more UL924 listed shunt relays to bypass local control devices during periodic and annual NFPA-mandated tests, in order to provide emergency power to designated emergency lighting fixtures.

    - Computer Port - The system shall include provisions to communicate inverter status and alarm conditions to a single computer or  across a computer network via optional network communication.

Part 5

5.1	Accessories (Optional Equipment)

    - Include normally off AC output bus for standby emergency lighting configured to illuminate in the event of a loss of commercial AC power or a remote input signal.

    - Include timed normally off AC output bus for standby emergency lighting configured to illuminate in the event of a loss of commercial AC power or a remote input signal.  Off bus “on” and “return” shall have configurable delay times.

    - Include automatic message dialer for telephone messaging to inform maintenance personnel of system alarm conditions for system on emergency battery power, low battery warning, or general alarm.

    - Include remote annunciator panel for remote status indication of system alarm conditions for system on emergency battery power, low battery warning, general alarm, and on static bypass. The annunciator panel shall be provided with an interface cable of (50) (100) (150) (200) feet to connect to the inverter communication port.

    - Include (SNMP / Ethernet TCP/IP / MODBUS TCP / BACnet/IP) (MODBUS RTU or ASCII over RS485 / BACnet MS/TP) for network communication of inverter system status and electrical measurement data.

    - Include (Quantity) control device (dimmer control, wall switch, occupancy sensor) override(s) for use with normally on inverter output bus to provide full illumination to designated emergency lights upon the failure or loss of commercial AC power.

    - Include (Quantity) zone sensing device(s) to sense voltage at individual zone lighting panels. The sensing device shall detect loss of power at the panel and shall signal the system to illuminate emergency fixtures within the specific zone only. If commercial AC power is acceptable at other zones, emergency lighting shall remain in the standby mode.

    - Include (quantity) pre-installed, 20 amp output circuit breakers for use with normally on AC output bus (Max. 20 pole positions between  normally on and normally off bus).

    - Include (quantity) pre-installed, 20 amp output circuit breakers for use with normally off AC output bus (Max. 20 pole positions between  normally on and normally off bus).

    - Include output circuit breaker open or tripped alarm contacts on all output circuit breakers for use with remote and/or local annunciation indicators (Each alarm contact adds ½ pole position to each breaker at 120 VAC to 277 VAC; therefore, a maximum of 13 pole positions. Adds 1 pole position to each breaker at 347 VAC; therefore, a maximum of 10 pole positions.)

Engineer’s Note: This monitored output circuit breaker option is mandatory for units installed in Canada.

    - Include a drip shield assembly to cover the Inverter (and battery) cabinet(s).

Engineer’s Note: A drip shield assembly is required for units installed in Canada.

Part 6

6.1	Warranty

    - The manufacturer shall guarantee all power component and system electronics to be free from defects in material and workmanship for a period of 2 years following shipment from the factory.

    - Battery warranty shall be 1 year full replacement, 14 years pro-rated.

6.2	Serviceability

Each inverter system contains one front-accessible electronics module subassembly. Batteries shall be positioned and wired to facilitate rapid replacement.

End of Guide Specification

(See Engineer’s Reference next pages)

| Engineer's Reference: BTU's / Hour, Weights, Dimensions |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| UL 924 LISTED MODELS W/ 90 MINUTES & C-UL LISTED MODELS W/ 30 MINUTES |  |  |  |  |  |  |  |
| kVA / kW |  | INPUT - OUTPUT VAC | BTU'S / HOUR FULL LOAD ¹ | BTU'S / HOUR STANDBY MODE ² | 90 MINUTE WEIGHTS (LBS) | 30 MINUTE WEIGHTS (LBS) |  |
| 1.5 |  | 120 - 120 | 511 | 128 | 898 | 744 |  |
| 1.5 |  | 277 - 277 |  |  | 1081 | 927 |  |
| 1.5 |  | 277 - 277/120 |  |  | 1081 | 927 |  |
| 2.2 |  | 120 - 120 | 750 | 188 | 898 | 744 |  |
| 2.2 |  | 277 - 277 |  |  | 1081 | 927 |  |
| 2.2 |  | 277 - 277/120 |  |  | 1081 | 927 |  |
| 3.0 |  | 120 - 120 | 1023 | 256 | 1073 | 697 |  |
| 3.0 |  | 208/120 - 208/120 |  |  | 1073 | 697 |  |
| 3.0 |  | 240/120 - 240/120 |  |  | 1073 | 697 |  |
| 3.0 |  | 277 - 277 |  |  | 1256 | 880 |  |
| 3.0 |  | 277 - 277/120 |  |  | 1256 | 880 |  |
| 3.5 |  | 120 - 120 | 1194 | 298 | 1073 | 775 |  |
| 3.5 |  | 208/120 - 208/120 |  |  | 1073 | 775 |  |
| 3.5 |  | 240/120 - 240/120 |  |  | 1073 | 775 |  |
| 3.5 |  | 277 - 277 |  |  | 1256 | 958 |  |
| 3.5 |  | 277 - 277/120 |  |  | 1256 | 958 |  |
| 4.2 |  | 120 - 120 | 2005 | 358 | 1459 | 1181 |  |
| 4.2 |  | 208/120 - 208/120 |  |  | 1459 | 1181 |  |
| 4.2 |  | 240/120 - 240/120 |  |  | 1459 | 1181 |  |
| 4.2 |  | 277 - 277 |  |  | 1645 | 1367 |  |
| 4.2 |  | 277 - 277/120 |  |  | 1645 | 1367 |  |
| 4.2 |  | 347 - 347/120 |  |  | 1645 | 1367 |  |
| 4.2 |  | 480 - 240/120 |  |  | 1645 | 1367 |  |
| 4.2 |  | 480 - 277 |  |  | 1645 | 1367 |  |
| 4.2 |  | 480 - 277/120 |  |  | 1645 | 1367 |  |
| 4.2 |  | 600 - 240/120 |  |  | 1645 | 1367 |  |
| 4.2 |  | 600 - 347/120 |  |  | 1645 | 1367 |  |
| 5.0 |  | 120 - 120 | 2387 | 426 | 1548 | 1181 |  |
| 5.0 |  | 208/120 - 208/120 |  |  | 1548 | 1181 |  |
| 5.0 |  | 240/120 - 240/120 |  |  | 1548 | 1181 |  |
| 5.0 |  | 277 - 277 |  |  | 1734 | 1367 |  |
| 5.0 |  | 277 - 277/120 |  |  | 1734 | 1367 |  |
| 5.0 |  | 347 - 347/120 |  |  | 1734 | 1367 |  |
| 5.0 |  | 480 - 240/120 |  |  | 1734 | 1367 |  |
| 5.0 |  | 480 - 277 |  |  | 1734 | 1367 |  |
| 5.0 |  | 480 - 277/120 |  |  | 1734 | 1367 |  |
| 5.0 |  | 600 - 240/120 |  |  | 1734 | 1367 |  |
| 5.0 |  | 600 - 347/120 |  |  | 1734 | 1367 |  |
| Cabinet Dimensions (Models 1.5 KW to 3.5 KW): 36"W x 24"D x 72"H |  |  |  |  |  |  |  |
| Cabinet Dimensions (Models 4.2 KW to 5.0 KW): 36"W x 24"D x 80"H |  |  |  |  |  |  |  |
| ¹ Full load BTU's represent worse case condition. 120V - 120V, 208/120V - 208/120V, and 240/120V - 240/120V models will have a lower BTU output. Consult factory for BTU’s / hour ratings on specific models. |  |  |  |  |  |  |  |
| ² Standby BTU’s represent emergency lighting loads that are normally off or turned off via a local control device, used together with a UL 924 listed bypass relay; or emergency lighting loads that switch from normal power to emergency power using a UL 1008 transfer relay device. Stated BTU’s for 120V, 208/120V, and 240/120V models. Consult factory for standby BTU’s on other models. |  |  |  |  |  |  |  |

| Engineer's Reference: BTU's / Hour, Weights, Dimensions |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| UL 924 LISTED MODELS W/ 90 MINUTES & C-UL LISTED MODELS W/ 30 MINUTES |  |  |  |  |  |  |  |
| kVA / kW |  | INPUT - OUTPUT VAC | BTU'S / HOUR FULL LOAD ¹ | BTU'S / HOUR STANDBY MODE ² | 90 MINUTE WEIGHTS (LBS) | 30 MINUTE WEIGHTS (LBS) |  |
| 6.0 |  | 208/120 - 208/120 | 2864 | 512 | 2004 | 1378 |  |
| 6.0 |  | 240/120 - 240/120 |  |  | 2004 | 1378 |  |
| 6.0 |  | 277 - 277 |  |  | 2254 | 1628 |  |
| 6.0 |  | 277 - 277/120 |  |  | 2254 | 1628 |  |
| 6.0 |  | 347 - 347/120 |  |  | 2254 | 1628 |  |
| 6.0 |  | 480 - 240/120 |  |  | 2254 | 1628 |  |
| 6.0 |  | 480 - 277 |  |  | 2254 | 1628 |  |
| 6.0 |  | 480 - 277/120 |  |  | 2254 | 1628 |  |
| 6.0 |  | 600 - 240/120 |  |  | 2254 | 1628 |  |
| 6.0 |  | 600 - 347/120 |  |  | 2254 | 1628 |  |
| 7.0 |  | 208/120 - 208/120 | 3342 | 597 | 2004 | 1378 |  |
| 7.0 |  | 240/120 - 240/120 |  |  | 2004 | 1378 |  |
| 7.0 |  | 277 - 277 |  |  | 2254 | 1628 |  |
| 7.0 |  | 277 - 277/120 |  |  | 2254 | 1628 |  |
| 7.0 |  | 347 - 347/120 |  |  | 2254 | 1628 |  |
| 7.0 |  | 480 - 240/120 |  |  | 2254 | 1628 |  |
| 7.0 |  | 480 - 277 |  |  | 2254 | 1628 |  |
| 7.0 |  | 480 - 277/120 |  |  | 2254 | 1628 |  |
| 7.0 |  | 600 - 240/120 |  |  | 2254 | 1628 |  |
| 7.0 |  | 600 - 347/120 |  |  | 2254 | 1628 |  |
| 7.5 |  | 208/120 - 208/120 | 3581 | 639 | 2630 | 1378 |  |
| 7.5 |  | 240/120 - 240/120 |  |  | 2630 | 1378 |  |
| 7.5 |  | 277 - 277 |  |  | 2808 | 1628 |  |
| 7.5 |  | 277 - 277/120 |  |  | 2808 | 1628 |  |
| 7.5 |  | 347 - 347/120 |  |  | 2808 | 1628 |  |
| 7.5 |  | 480 - 240/120 |  |  | 2808 | 1628 |  |
| 7.5 |  | 480 - 277 |  |  | 2808 | 1628 |  |
| 7.5 |  | 480 - 277/120 |  |  | 2808 | 1628 |  |
| 7.5 |  | 600 - 240/120 |  |  | 2808 | 1628 |  |
| 7.5 |  | 600 - 347/120 |  |  | 2808 | 1628 |  |
| 90 Minute - Cabinet Dimensions (Models 6.0 KW to 7.0 KW): 36"W x 24"D x 80"H |  |  |  |  |  |  |  |
| 90 Minute - Cabinet Dimensions (Models 7.5 KW): 65"W x 24"D x 80"H |  |  |  |  |  |  |  |
| 30 Minute - Cabinet Dimensions (Models 6.0 KW to 7.5 KW): 36"W x 24"D x 80"H |  |  |  |  |  |  |  |
| ¹ Full load BTU's represent worse case condition. 120V - 120V, 208/120V - 208/120V, and 240/120V - 240/120V models will have a lower BTU output. Consult factory for BTU’s / hour ratings on specific models. |  |  |  |  |  |  |  |
| ² Standby BTU’s represent emergency lighting loads that are normally off or turned off via a local control device, used together with a UL 924 listed bypass relay; or emergency lighting loads that switch from normal power to emergency power using a UL 1008 transfer relay device. Stated BTU’s for 120V, 208/120V, and 240/120V models. Consult factory for standby BTU’s on other models. |  |  |  |  |  |  |  |

| Engineer's Reference: BTU's / Hour, Weights, Dimensions |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| UL 924 LISTED MODELS W/ 90 MINUTES & C-UL LISTED MODELS W/ 30 MINUTES |  |  |  |  |  |  |
| kVA / kW |  | INPUT - OUTPUT VAC | BTU'S / HOUR FULL LOAD ¹ | BTU'S / HOUR STANDBY MODE ² | 90 MINUTE WEIGHTS (LBS) | 30 MINUTE WEIGHTS (LBS) |
| 8.5 |  | 208/120 - 208/120 | 4058 | 725 | 2648 | 1396 |
| 8.5 |  | 240/120 - 240/120 |  |  | 2648 | 1396 |
| 8.5 |  | 277 - 277 |  |  | 2898 | 2046 |
| 8.5 |  | 277 - 277/120 |  |  | 2898 | 2046 |
| 8.5 |  | 347 - 347/120 |  |  | 2898 | 2046 |
| 8.5 |  | 480 - 240/120 |  |  | 2898 | 2046 |
| 8.5 |  | 480 - 277 |  |  | 2898 | 2046 |
| 8.5 |  | 480 - 277/120 |  |  | 2898 | 2046 |
| 8.5 |  | 600 - 240/120 |  |  | 2898 | 2046 |
| 8.5 |  | 600 - 347/120 |  |  | 2898 | 2046 |
| 10 |  | 208/120 - 208/120 | 4774 | 853 | 3048 | 1509 |
| 10 |  | 240/120 - 240/120 |  |  | 3048 | 1509 |
| 10 |  | 277 - 277 |  |  | 3298 | 2159 |
| 10 |  | 277 - 277/120 |  |  | 3298 | 2159 |
| 10 |  | 347 - 347/120 |  |  | 3298 | 2159 |
| 10 |  | 480 - 240/120 |  |  | 3298 | 2159 |
| 10 |  | 480 - 277 |  |  | 3298 | 2159 |
| 10 |  | 480 - 277/120 |  |  | 3298 | 2159 |
| 10 |  | 600 - 240/120 |  |  | 3298 | 2159 |
| 10 |  | 600 - 347/120 |  |  | 3298 | 2159 |
| 12.5 |  | 208/120 - 208/120 | 5967 | 1065 | 3684 | 1861 |
| 12.5 |  | 240/120 - 240/120 |  |  | 3684 | 1861 |
| 12.5 |  | 277 - 277 |  |  | 4124 | 2541 |
| 12.5 |  | 277 - 277/120 |  |  | 4124 | 2541 |
| 12.5 |  | 347 - 347/120 |  |  | 4124 | 2541 |
| 12.5 |  | 480 - 240/120 |  |  | 4124 | 2541 |
| 12.5 |  | 480 - 277 |  |  | 4124 | 2541 |
| 12.5 |  | 480 - 277/120 |  |  | 4124 | 2541 |
| 12.5 |  | 600 - 240/120 |  |  | 4124 | 2541 |
| 12.5 |  | 600 - 347/120 |  |  | 4124 | 2541 |

| 90 Minute - Cabinet Dimensions (Models 8.5 KW to 10 KW): 65"W x 24"D x 80"H |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 90 Minute - Cabinet Dimensions (Model 12.5 KW): 72"W x 27"D x 80"H |  |  |  |  |  |  |
| 30 Minute - Cabinet Dimensions (Models 10 KW to 12.5 KW), 208/120 or 240/120 VAC input - output: 36"W x 24"D x 80"H |  |  |  |  |  |  |
| 30 Minute - Cabinet Dimensions (Models 10 KW to 12.5 KW), all other voltage configurations: 65"W x 24"D x 80"H |  |  |  |  |  |  |
| ¹ Full load BTU's represent worse case condition. 120V - 120V, 208/120V - 208/120V, and 240/120V - 240/120V models will have a lower BTU output. Consult factory for BTU’s / hour ratings on specific models. |  |  |  |  |  |  |
| ² Standby BTU’s represent emergency lighting loads that are normally off or turned off via a local control device, used together with a UL 924 listed bypass relay; or emergency lighting loads that switch from normal power to emergency power using a UL 1008 transfer relay device. Stated BTU’s for 120V, 208/120V, and 240/120V models. Consult factory for standby BTU’s on other models. |  |  |  |  |  |  |

| Engineer's Reference: BTU's / Hour, Weights, Dimensions |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| UL 924 LISTED MODELS W/ 90 MINUTES & C-UL LISTED MODELS W/ 30 MINUTES |  |  |  |  |  |  |
| kVA / kW |  | INPUT - OUTPUT VAC | BTU'S / HOUR FULL LOAD ¹ | BTU'S / HOUR STANDBY MODE ² | 90 MINUTE WEIGHTS (LBS) | 30 MINUTE WEIGHTS (LBS) |
| 13.5 |  | 208/120 - 208/120 | 6445 | 1151 | 3694 | 1861 |
| 13.5 |  | 240/120 - 240/120 |  |  | 3694 | 1861 |
| 13.5 |  | 277 - 277 |  |  | 4134 | 2541 |
| 13.5 |  | 277 - 277/120 |  |  | 4134 | 2541 |
| 13.5 |  | 347 - 347/120 |  |  | 4134 | 2541 |
| 13.5 |  | 480 - 240/120 |  |  | 4134 | 2541 |
| 13.5 |  | 480 - 277 |  |  | 4134 | 2541 |
| 13.5 |  | 480 - 277/120 |  |  | 4134 | 2541 |
| 13.5 |  | 600 - 240/120 |  |  | 4134 | 2541 |
| 13.5 |  | 600 - 347/120 |  |  | 4134 | 2541 |
| 14 |  | 208/120 - 208/120 | 6684 | 1194 | 4136 | 1861 |
| 14 |  | 240/120 - 240/120 |  |  | 4136 | 1861 |
| 14 |  | 277 - 277 |  |  | 4576 | 2541 |
| 14 |  | 277 - 277/120 |  |  | 4576 | 2541 |
| 14 |  | 347 - 347/120 |  |  | 4576 | 2541 |
| 14 |  | 480 - 240/120 |  |  | 4576 | 2541 |
| 14 |  | 480 - 277 |  |  | 4576 | 2541 |
| 14 |  | 480 - 277/120 |  |  | 4576 | 2541 |
| 14 |  | 600 - 240/120 |  |  | 4576 | 2541 |
| 14 |  | 600 - 347/120 |  |  | 4576 | 2541 |

| 90 Minute - Cabinet Dimensions (Models 13.5 KW to 14 KW): 72"W x 27"D x 80"H |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 30 Minute - Cabinet Dimensions (Models 13.5 KW to 14 KW), 208/120 or 240/120 VAC input - output: 36"W x 24"D x 80"H |  |  |  |  |  |  |
| 30 Minute - Cabinet Dimensions (Models 13.5 KW to 14 KW), all other voltage configurations: 65"W x 24"D x 80"H |  |  |  |  |  |  |
| ¹ Full load BTU's represent worse case condition. 120V - 120V, 208/120V - 208/120V, and 240/120V - 240/120V models will have a lower BTU output. Consult factory for BTU’s / hour ratings on specific models. |  |  |  |  |  |  |
| ² Standby BTU’s represent emergency lighting loads that are normally off or turned off via a local control device, used together with a UL 924 listed bypass relay; or emergency lighting loads that switch from normal power to emergency power using a UL 1008 transfer relay device. Stated BTU’s for 120V, 208/120V, and 240/120V models. Consult factory for standby BTU’s on other models. |  |  |  |  |  |  |